## EIA proxies
Fuel codes from EIA form 923
EIA Code | EIA Definition | Proxy for this work | Code
LFG | Landfill Gas | Gaseous Biomass | BMG
OBG | Other Biomass Gas. Including digester gas, methane, and other biomass gases. | Gaseous Biomass | BMG
AB | Agricultural By-Products | Non-gaseous Biomass | BM
BLQ | Black Liquor | Non-gaseous Biomass | BM
MSB | Biogenic Municipal Solid Waste | Non-gaseous Biomass | BM
MSN | Non-biogenic Municipal Solid Waste | Non-gaseous Biomass | BM
OBL | Other Biomass Liquids | Non-gaseous Biomass | BM
OBS | Other Biomass Solids | Non-gaseous Biomass | BM
SLW | Sludge Waste | Non-gaseous Biomass | BM
TDF | Tire-derived Fuels | Non-gaseous Biomass | BM
WDL | Wood Waste Liquids, excluding Black Liquor. Including red liquor, sludge wood, spent sulfite liquor, and other wood-based liquids. | Non-gaseous Biomass | BM
WDS | Wood/Wood Waste Solids. Including paper pellets, railroad ties, utility polies, wood chips, bark, and other wood waste solids. | Non-gaseous Biomass | BM
BIT | Bituminous Coal | Non-gaseous Fossil | FSL
DFO | Distillate Fuel Oil. Including diesel, No. 1, No. 2, and No. 4 fuel oils. | Non-gaseous Fossil | FSL
JF | Jet Fuel | Non-gaseous Fossil | FSL
KER | Kerosene | Non-gaseous Fossil | FSL
LIG | Lignite Coal | Non-gaseous Fossil | FSL
PC | Petroleum Coke | Non-gaseous Fossil | FSL
RC | Refined Coal | Non-gaseous Fossil | FSL
RFO | Residual Fuel Oil. Including No. 5 & 6 fuel oils and bunker C fuel oil. | Non-gaseous Fossil | FSL
SC | Coal-based Synfuel. Including briquettes, pellets, or extrusions, which are formed by binding materials or processes that recycle materials. | Non-gaseous Fossil | FSL
SUB | Subbituminous Coal | Non-gaseous Fossil | FSL
WC | Waste/Other Coal. Including anthracite culm, bituminous gob, fine coal, lignite waste, waste coal. | Non-gaseous Fossil | FSL
WO | Waste/Other Oil. Including crude oil, liquid butane, liquid propane, naphtha, oil waste, re-refined moto oil, sludge oil, tar oil, or other petroleum-based liquid wastes. | Non-gaseous Fossil | FSL
GEO | Geothermal | Geothermal | GEO
BFG | Blast Furnace Gas | Gaseous Fossil | FSLG
NG | Natural Gas | Gaseous Fossil | FSLG
PG | Gaseous Propane | Gaseous Fossil | FSLG
SGC | Coal-Derived Synthesis Gas | Gaseous Fossil | FSLG
SGP | Synthesis Gas from Petroleum Coke | Gaseous Fossil | FSLG
OG | Other Gas | Gaseous Fossil | FSLG
NUC | Nuclear. Including Uranium, Plutonium, and Thorium. | Nuclear | NUC
SUN | Solar | Solar | SUN
WAT | Water at a Conventional Hydroelectric Turbine and water used in Wave Buoy Hydrokinetic Technology, current Hydrokinetic Technology, Tidal Hydrokinetic Technology, and Pumping Energy for Reversible (Pumped Storage) Hydroelectric Turbines. | Hydro | WAT
WND | Wind | Wind | WND
ANT | Anthracite Coal | n/a
MWH | Electricity used for energy storage | n/a
OTH | Other Fuel |  | OTH
PUR | Purchased Steam |  | OTH
WH | Waste Heat not directly attributed to a fuel source |  | OTH
Prime mover codes from EIA form 923
EIA Code | EIA Definition | Proxy for this work | Code
CA | Combined-Cycle -- Steam Part | Combined Cycle | CC
CS | Combined-Cycle Single-Shaft Combustion Turbine and Steam Turbine share of single generator | Combined Cycle | CC
CT | Combined-Cycle Combustion Turbine Part | Combined Cycle | CC
BA | Energy Storage, Battery | Energy Storage | ES
CE | Energy Storage, Compressed Air | Energy Storage | ES
CP | Energy Storage, Concentrated Solar Power | Energy Storage | ES
ES | Energy Storage, Other (Specify on Schedule 9, Comments) | Energy Storage | ES
FW | Energy Storage, Flywheel | Energy Storage | ES
PS | Energy Storage, Reversible Hydraulic Turbine (Pumped Storage) | Energy Storage | ES
GT | Combustion (Gas) Turbine. Including Jet Engine design | Combustion Turbine | GT
IC | Internal Combustion (diesel, piston, reciprocating) Engine | Combustion Turbine | GT
HA | Hydrokinetic, Axial Flow Turbine | Hydrokinetic | HK
HB | Hydrokinetic, Wave Buoy | Hydrokinetic | HK
HK | Hydrokinetic, Other | Hydrokinetic | HK
HY | Hydraulic Turbine. Including turbines associated with delivery of water by pipeline. | Hydraulic | HY
PV | Photovoltaic | Photovoltaic | PV
BT | Turbines Used in a Binary Cycle. Including those used for geothermal applications | Steam Turbine | ST
ST | Steam Turbine. Including Nuclear, Geothermal, and Solar Steam (does not include Combined Cycle). | Steam Turbine | ST
WT | Wind Turbine, Onshore | Wind Turbine | WT
WS | Wind Turbine, Offshore | Wind Turbine | WT
FC | Fuel Cell
OT | Other |  | OT
Cooling System codes from EIA form 923
EIA Code | EIA Definition | Proxy for this work | Code
DC | Dry (air) cooling System | Dry cooling | DC
H | Hybrid (non-specified) | Hybrid | HB
HRC | Hybrid: recirculating cooling pond(s) or canal(s) with dry cooling | Hybrid | HB
HRF | Hybrid: recirculating with forced draft cooling tower(s) with dry cooling | Hybrid | HB
HRI | Hybrid: recirculating with induced draft cooling tower(s) with dry cooling | Hybrid | HB
HT | Helper Tower | Recirculating | RC
O | Once through (non-specified) | Once through | ON
O + R | Once through (non-specified) and Recirculating (non-specified) | Once through | ON
OC | Once through with Cooling Ponds | Pond | PN
ON | Once through without cooling pond(s) or canal(s) | Once through | ON
OT | Other - Specify in Footnote
R | Recirculating (non-specified) | Recirculating | RC
RC | Recirculating with Cooling Ponds | Pond | PN
RF | Recirculating with Forced Draft Cooling Tower | Recirculating | RC
RI | Recirculating with Induced Draft Cooling Tower | Recirculating | RC
RN | Recirculating with Natural Draft Cooling Tower | Recirculating | RC

## water use rates
Code | Fuel | Prime.Mover | Cooling.System | CHP.Status | Water.Consumption.galMWh | Water.Withdrawal.galMwh | WC.m3GJ | WW.m3GJ | notes
BM_GT_NA_N | BM | GT | NA | N | 0 | 0 |  |  | No cooling required
BM_ST_DC_N | BM | ST | DC | N | 0 | 0 |  |  | 10% of recirculaing (tower) rate
BM_ST_DC_Y | BM | ST | DC | Y | 36.3 | 3792.4 |  |  | 10% of recirculaing (tower) rate
BM_ST_NA_N | BM | ST | NA | N | 5.8546 | 125.842 | 0.079783 | 1.7149 | Water use rates from EG & KTS for Solid Biomass & RDF
BM_ST_NA_Y | BM | ST | NA | Y | 5.8546 | 125.842 | 0.079783 | 1.7149 | Water use rates from EG & KTS for Solid Biomass & RDF
BM_ST_ON_N | BM | ST | ON | N | 5.8546 | 125.842 | 0.079783 | 1.7149 | Water use rates from EG & KTS for Solid Biomass & RDF
BM_ST_ON_Y | BM | ST | ON | Y | 5.8546 | 125.842 | 0.079783 | 1.7149 | Water use rates from EG & KTS for Solid Biomass & RDF
BM_ST_PN_N | BM | ST | PN | N | 5.8546 | 125.842 | 0.079783 | 1.7149 | Water use rates from EG & KTS for Solid Biomass & RDF
BM_ST_PN_Y | BM | ST | PN | Y | 5.8546 | 125.842 | 0.079783 | 1.7149 | Water use rates from EG & KTS for Solid Biomass & RDF
BM_ST_RC_N | BM | ST | RC | N | 5.8546 | 125.842 | 0.079783 | 1.7149 | Water use rates from EG & KTS for Solid Biomass & RDF
BM_ST_RC_Y | BM | ST | RC | Y | 5.8546 | 125.842 | 0.079783 | 1.7149 | Water use rates from EG & KTS for Solid Biomass & RDF
BMG_ES_NA_N | BMG | ES | NA | N | 0 | 0 |  |  | No cooling required
BMG_ES_NA_Y | BMG | ES | NA | Y | 0 | 0 |  |  | No cooling required
BMG_GT_NA_N | BMG | GT | NA | N | 0 | 0 |  |  | No cooling required
BMG_GT_NA_Y | BMG | GT | NA | Y | 0 | 0 |  |  | No cooling required
BMG_GT_RC_Y | BMG | GT | RC | Y | 0 | 0 |  |  | No cooling required
BMG_OT_NA_Y | BMG | OT | NA | Y | 3.3777 | 125.842 | 0.046029 | 1.7149 | Water use rates from EG & KTS for Biogas
BMG_ST_DC_N | BMG | ST | DC | N | 0 | 0 |  |  | 10% of recirculaing (tower) rate
BMG_ST_NA_N | BMG | ST | NA | N | 3.3777 | 125.842 | 0.046029 | 1.7149 | Water use rates from EG & KTS for Biogas
BMG_ST_NA_Y | BMG | ST | NA | Y | 3.3777 | 125.842 | 0.046029 | 1.7149 | Water use rates from EG & KTS for Biogas
BMG_ST_ON_N | BMG | ST | ON | N | 3.3777 | 125.842 | 0.046029 | 1.7149 | Water use rates from EG & KTS for Biogas
BMG_ST_ON_Y | BMG | ST | ON | Y | 3.3777 | 125.842 | 0.046029 | 1.7149 | Water use rates from EG & KTS for Biogas
BMG_ST_RC_N | BMG | ST | RC | N | 3.3777 | 125.842 | 0.046029 | 1.7149 | Water use rates from EG & KTS for Biogas
BMG_ST_RC_Y | BMG | ST | RC | Y | 3.3777 | 125.842 | 0.046029 | 1.7149 | Water use rates from EG & KTS for Biogas
FSL_CC_NA_N | FSL | CC | NA | N | 0 | 0 |  |  | Assume recirculating cooling system. 110% of Peer et al. (2016) water use rates for Natural Gas Single Shaft
FSL_CC_RC_N | FSL | CC | RC | N | 0 | 0 |  |  | 110% of Peer et al. (2016) water use rates for Natural Gas CC single shaft
FSL_GT_HB_N | FSL | GT | HB | N | 0 | 0 |  |  | No cooling required
FSL_GT_NA_N | FSL | GT | NA | N | 0 | 0 |  |  | No cooling required
FSL_GT_NA_Y | FSL | GT | NA | Y | 0 | 0 |  |  | No cooling required
FSL_GT_ON_N | FSL | GT | ON | N | 0 | 0 |  |  | No cooling required
FSL_GT_PN_N | FSL | GT | PN | N | 0 | 0 |  |  | No cooling required
FSL_GT_RC_N | FSL | GT | RC | N | 0 | 0 |  |  | No cooling required
FSL_GT_RC_Y | FSL | GT | RC | Y | 0 | 0 |  |  | No cooling required
FSL_OT_NA_Y | FSL | OT | NA | Y | 0 | 0 |  |  | Assume no cooling system required
FSL_ST_DC_N | FSL | ST | DC | N | 0 | 0 |  |  | 10% of recirculaing (tower) rate
FSL_ST_DC_Y | FSL | ST | DC | Y | 0 | 0 |  |  | 10% of recirculaing (tower) rate
FSL_ST_HB_Y | FSL | ST | HB | Y | 392 | 470 |  |  | Peer et al. (2016) water use rates for Coal
FSL_ST_NA_N | FSL | ST | NA | N | 0 | 0 |  |  | Assume once through cooling system. Peer et al (2016) water use rates for coal
FSL_ST_NA_Y | FSL | ST | NA | Y | 0 | 0 |  |  | Assume once through cooling system. Peer et al (2016) water use rates for coal
FSL_ST_ON_N | FSL | ST | ON | N | 204 | 41106 |  |  | Peer et al. (2016) water use rates for Coal
FSL_ST_ON_Y | FSL | ST | ON | Y | 1997 | 60940 |  |  | Peer et al. (2016) water use rates for Coal
FSL_ST_PN_N | FSL | ST | PN | N | 368 | 35338 |  |  | Peer et al. (2016) water use rates for Coal recirculating ponds, no CHP
FSL_ST_PN_Y | FSL | ST | PN | Y | 368 | 35338 |  |  | Peer et al. (2016) water use rates for Coal recirculating ponds, no CHP
FSL_ST_RC_N | FSL | ST | RC | N | 487 | 539 |  |  | Peer et al. (2016) water use rates for Coal
FSL_ST_RC_Y | FSL | ST | RC | Y | 487 | 546 |  |  | Peer et al. (2016) water use rates for Coal
FSLG_CC_DC_N | FSLG | CC | DC | N | 0 | 0 |  |  | 10% of recirculaing (tower) rate
FSLG_CC_NA_N | FSLG | CC | NA | N | 205 | 227 |  |  | Assume recirculating cooling system. Peer et al. (2016) water use rates for Natural Gas Single Shaft
FSLG_CC_NA_Y | FSLG | CC | NA | Y | 238 | 273 |  |  | Assume recirculating cooling system. Peer et al. (2016) water use rates for Natural Gas Single Shaft
FSLG_CC_RC_N | FSLG | CC | RC | N | 205 | 227 |  |  | Peer et al. (2016) water use rates for Natural Gas CC single shaft
FSLG_ES_NA_N | FSLG | ES | NA | N | 0 | 0 |  |  | No cooling required
FSLG_ES_NA_Y | FSLG | ES | NA | Y | 0 | 0 |  |  | No cooling required
FSLG_GT_DC_N | FSLG | GT | DC | N | 0 | 0 |  |  | No cooling required
FSLG_GT_HB_N | FSLG | GT | HB | N | 0 | 0 |  |  | No cooling required
FSLG_GT_NA_N | FSLG | GT | NA | N | 0 | 0 |  |  | No cooling required
FSLG_GT_NA_Y | FSLG | GT | NA | Y | 0 | 0 |  |  | No cooling required
FSLG_GT_ON_N | FSLG | GT | ON | N | 0 | 0 |  |  | No cooling required
FSLG_GT_PN_N | FSLG | GT | PN | N | 0 | 0 |  |  | No cooling required
FSLG_GT_RC_N | FSLG | GT | RC | N | 0 | 0 |  |  | No cooling required
FSLG_GT_RC_Y | FSLG | GT | RC | Y | 0 | 0 |  |  | No cooling required
FSLG_OT_NA_N | FSLG | OT | NA | N | 0 | 0 |  |  | Assume no cooling system required
FSLG_OT_NA_Y | FSLG | OT | NA | Y | 0 | 0 |  |  | Assume no cooling system required
FSLG_ST_DC_N | FSLG | ST | DC | N | 0 | 0 |  |  | 10% of recirculaing (tower) rate
FSLG_ST_DC_Y | FSLG | ST | DC | Y | 0 | 0 |  |  | 10% of recirculaing (tower) rate
FSLG_ST_HB_N | FSLG | ST | HB | N | 92 | 93 |  |  | Peer et al. (2016) water use rates for Natural Gas
FSLG_ST_HB_Y | FSLG | ST | HB | Y | 200 | 325 |  |  | Peer et al. (2016) water use rates for Natural Gas
FSLG_ST_NA_N | FSLG | ST | NA | N | 363 | 37924 |  |  | Assume once through cooling system. Peer et al (2016) water use rates for natural gas
FSLG_ST_NA_Y | FSLG | ST | NA | Y | 0 | 0 |  |  | Assume once through cooling system. Peer et al (2016) water use rates for natural gas
FSLG_ST_ON_N | FSLG | ST | ON | N | 325 | 118490 |  |  | Peer et al. (2016) water use rates for Natural Gas
FSLG_ST_ON_Y | FSLG | ST | ON | Y | 325 | 118490 |  |  | Peer et al. (2016) water use rates for Natural Gas with no CHP
FSLG_ST_PN_N | FSLG | ST | PN | N | 317 | 149449 |  |  | Peer et al. (2016) water use rates for Natural Gas recirculating ponds, no CHP
FSLG_ST_PN_Y | FSLG | ST | PN | Y | 317 | 149449 |  |  | Peer et al. (2016) water use rates for Natural Gas recirculating ponds, no CHP
FSLG_ST_RC_N | FSLG | ST | RC | N | 833 | 1235 |  |  | Peer et al. (2016) water use rates for Natural Gas
FSLG_ST_RC_Y | FSLG | ST | RC | Y | 833 | 1235 |  |  | Peer et al. (2016) water use rates for Natural Gas, no CHP
GEO_BT_NA_N | GEO | BT | NA | N | 19.6336 | 19.6336 | 0.26756 | 0.26756 | Water use rates from EG & KTS for Geothermal binary turbine wet cooled
GEO_ST_NA_N | GEO | ST | NA | N | 2.8688 | 2.8688 | 0.039095 | 0.039095 | Water use rates from EG & KTS for Geothermal wet cooled
GEO_ST_NA_Y | GEO | ST | NA | Y | 2.8688 | 2.8688 | 0.039095 | 0.039095 | Water use rates from EG & KTS for Geothermal wet cooled
NUC_ST_NA_N | NUC | ST | NA | N | 363 | 37924 |  |  | Assume once through cooling system. Peer et al (2016) water use rates for nuclear
OTH_GT_NA_N | OTH | GT | NA | N | 0 | 0 |  |  | No cooling required
OTH_GT_NA_Y | OTH | GT | NA | Y | 0 | 0 |  |  | No cooling required
OTH_OT_NA_N | OTH | OT | NA | N | 0 | 0 |  |  | Assume no cooling system required
OTH_OT_NA_Y | OTH | OT | NA | Y | 0 | 0 |  |  | Assume no cooling system required
OTH_ST_NA_N | OTH | ST | NA | N | 363 | 37924 |  |  | Assume once through cooling system. Peer et al (2016) water use rates for natural gas
OTH_ST_NA_Y | OTH | ST | NA | Y | 0 | 0 |  |  | Assume once through cooling system. Peer et al (2016) water use rates for natural gas
OTH_ST_ON_N | OTH | ST | ON | N | 363 | 37924 |  |  | Peer et al. (2016) water use rates for Natural Gas
OTH_ST_ON_Y | OTH | ST | ON | Y | 0 | 0 |  |  | Peer et al. (2016) water use rates for Natural Gas
OTH_ST_PN_N | OTH | ST | PN | N | 363 | 37924 |  |  | Peer et al. (2016) water use rates for Coal recirculating ponds, no CHP
OTH_ST_RC_N | OTH | ST | RC | N | 0 | 0 |  |  | Peer et al. (2016) water use rates for Natural Gas
OTH_ST_RC_Y | OTH | ST | RC | Y | 363 | 37924 |  |  | Peer et al. (2016) water use rates for Natural Gas, no CHP
SUN_ES_NA_N | SUN | ES | NA | N | 0 | 0 |  |  | No cooling required
SUN_PV_NA_N | SUN | PV | NA | N | 0 | 0 |  |  | No cooling required
SUN_PV_NA_Y | SUN | PV | NA | Y | 0 | 0 |  |  | No cooling required
SUN_ST_NA_N | SUN | ST | NA | N | 786 | 786 |  |  | Macknick value
WAT_ES_NA_N | WAT | ES | NA | N | 0 | 0 |  |  | No cooling required
WAT_HY_NA_N | WAT | HY | NA | N | 0 | 0 |  |  | No cooling required
WAT_HY_NA_Y | WAT | HY | NA | Y | 0 | 0 |  |  | No cooling required
WND_WT_NA_N | WND | WT | NA | N | 0 | 0 |  |  | No cooling required
WND_WT_NA_Y | WND | WT | NA | Y | 0 | 0 |  |  | No cooling required
NA_ES_NA_N | NA | ES | NA | N | 0 | 0 |  |  | No cooling required
NA_GT_NA_N | NA | GT | NA | N | 0 | 0 |  |  | No cooling required
NA_ST_NA_N | NA | ST | NA | N | 2.8688 | 2.8688 |  |  | Assume once through cooling system. Peer et al (2016) water use rates for natural gas
NA_ST_NA_Y | NA | ST | NA | Y | 0 | 0 |  |  | Assume once through cooling system. Peer et al (2016) water use rates for natural gas